## Table 1
Solar HUPS PWM TECHNICAL SPECIFICATIONS
S. No. | Parameter | Unit | Rating
1 | Model name |  | SunSine Pro 950 | SunSine Pro 1150 | SunSine Pro 1450 | SunSine Pro 1750 | SunSine Pro 2550 | SunSine Pro 2950
2 | System rating (Name Plate) | VA | 700 | 900 | 1100 | 1450 | 2100 | 2500
3 | Full Load Input Current ±2A | Amp | 45 | 55 | 65 | 51 | 65 | 65
4 | Operating DC voltage | V | 12 |  |  | 24
5 | Input voltage max Voc | Vdc | 25 |  |  | 45
6 | Maximum Solar array power | Wp | 700 | 900 | 1000 | 1600 | 2000 | 2500
7 | Max PV modules | Nos | 4(165W) | 4(165W) | 6(165W) | 5(335W) | 5(335W) | 8(335W)
8 | Modules in series | Nos | NO
9 | Parallel strings | Nos | 2 | 5 | 6 | 5 | 6 | 6
10 | Switching element in SCC |  | MOSFET
11 | Type of control |  | Micro
12 | Type of solar charger |  | PWM
13 | Max current rating of SCC | Adc | 40 |  |  |  | 50 | 70
14 | Efficiency of MPP tracking | % | NA
15 | Efficiency of SCC | % | >90
16 | Switching element in Inverter |  | MOSFET
17 | Type of Control |  | PWM
18 | Nominal Output voltage in inverter mode | Vac | 220V ± 7V
19 | Output supply phases |  | single
20 | Nominal Output Frequency of Inverter | Hz | 50/60 ± 1 (Default is 50Hz) selectable 50/60Hz (Optional)
21 | Frequency (Min - Max during Grid by pass) UPS mode | Hz | 47-53/57-63
22 | Frequency (Min - Max during Grid by pass) Inverter mode | Hz | 40-60/50-70
23 | Output voltage regulation | % | 180-220
24 | Output THD (v) at linear load | % | <5%
25 | Creast Factor |  | 3:01
26 | Overload capacity 125% | Sec | 6 (6 Retry)
27 | Overload capacity 150% | Sec | 2 (6 Retry)
28 | Cooling Fan ON at temp | ⁰C | 60 (or 45% of rated Load or Solar I>15A)
29 | Cooling Fan Off at temp | ⁰C | 55 (or 40% of rated Load or Solar I<15A)
30 | Peak efficiency of inverter | % | 82 | 82 | 81 | 81 | 81 | 81
31 | Battery low voltage alarm per battery | Vdc | 10.8 ± 0.2
32 | Battery low voltage cut per battery | Vdc | 10.5 ± 0.2 (With 4 Retry)
33 | Batter low cut recovery per battery through Solar | Vdc | 12.7 ± 0.2 (or Mains or reset swich on front panel)
34 | Max Battery charging voltage by grid per battery | Vdc | 14.4 ± 0.2 settable for Tub-14.4V/28.8V, GEL-14.2V/28.4V, SMF-14.2V/28.4, Flat-14.2V/28.4V settable for Tub-13.8V/27.6V, GEL-13.8V/27.6V, SMF-13.8V/27.6, Flat-13.6V/27.2V
35 | Max Battery charging current by grid in Hi/Lo option | Adc | 16/12 ±2A settable for Tub-12/16A, GEL-10/16A, SMF-10/14A, Flat-14/10
36 | Max Battery charging voltage by Solar per battery | Vdc | 14.4 ± 0.2 settable for Tub-14.4V/28.8V, GEL-14.2V/28.4V, SMF-14.2V/28.4, Flat-14.2V/28.4V settable for Tub-13.8V/27.6V, GEL-13.8V/27.6V, SMF-13.8V/27.6, Flat-13.6V/27.2V
37 | Battery High cut with Alarm per battery | Vdc | 15.5±0.2
38 | Battery High cut Recovery per battery | Vdc | 14.5±0.2
39 | Max Battery charging current by Solar | Adc | 20±2A
40 | Max Charging current to battery by Solar+Grid | Adc | 20±2A
41 | Grid low cut voltage (IT load/Normal load) | Vac | 180/100 ± 10
42 | Grid low cut voltage recovery (IT load/Normal load) | Vac | 190/110 ± 10
43 | Grid high cut voltage (IT load/Normal load) | Vac | 265/280 ± 10
44 | Grid high cut voltage recovery (IT load/Normal load) | Vac | 255/270 ± 10

## Table 2
46 | Grid charging Enable/Disable |  | yes
47 | Selection of UPS Load/Normal Load |  | yes
48 | Selection of Operating Mode |  | HC-Charging current = 20A ±1A Solar + Mains till battery boost voltage with maximum Solar Sharing. System will not be disconnect Grid in any case
EC-Charging current= 20A ±1A Solar + Mains till boost voltage, System will cut off the mains when battery voltage reaches boost voltage level and output load is transferred to Solar + Battery and Grid reconnected <=11.8V/11.2V per Battery.
SC-Charging current= 20A ±1A Solar + Mains till boost voltage, System will cut off the mains when battery voltage reaches boost voltage level and output load is transferred to Solar + Battery and Grid reconnected <=12.0V per Battery or Solar fails or if Solar <5A check if Solar < discharging connect grid
49 | Output Voltage at No load at rated Battery voltage | Vac | 220
50 | Output Voltage at 100% load at Nominal Battery voltage | Vac | 200±5 | 200±5 | 200±5 | 200±5 | 200±5 | 200±5 | 200±5
51 | Input current at no load at Nominal Battery voltage | Adc | 2.2 | 2.6 | 2.4 | 2.2 | 2.5 | 2.2 | 2.8
52 | Noise @ 1 meter | dB | <50
53 | Protections |  | Overload, Battery Deep discharge,Battery Overcharge,Short circuit(1retry),Battery Hi,PV Reverse,Over Temp,Fuse Trip,battery reverse
54 | LCD Display parameters |  | PV Current, Battery voltage, Mains voltage, UPS ON/OFF, UPS Mode, Symbol of sun (Smily) if solar available, (non smily symbol in absence of solar), Load percentage (0 to 150%), over load, short ckt, fault, battery low, over temp, PV reverse, Fuse trip, (Customised LCD )
55 | Indication LEDs |  | Tact switch Status
56 | Operating Temperature range | ⁰C | 0-50
57 | Storage Temperature range | ⁰C | 0 +65
58 | Max RH | % | 95
59 | Front panel details ( MCB, Display, Selection switch etc) |  | Display with tact switch
60 | Rear panel details (MCB, Terminals etc) |  | O/P socket,fuse/Circuit breaker,mains & batt. Cable and fan |  |  |  |  | O/P socket,fuse/Circuit breaker,mains & batt. Cable and fan,Terminal
61 | Enclosure protection | IP | 20
62 | Changeover time from inverter to mains in UPS mode | ms | <10
63 | Changeover time from inverter to mains in Normal mode | ms | <10
64 | Changeover time from mains to inverter in UPS mode | ms | <10
65 | Changeover time from mains to inverter in Normal mode | ms | <40
66 | Battery connection |  | thru Copper cable 10 sqmm and 1mtr red 0.7mtr black length |  | thru Copper cable 16 sqmm and 1mtr red 0.8mtr black length | thru Copper cable 10 sqmm and 1.25mtr red 1mtr black length |  | thru Copper cable 16 sqmm and 1.25mtr red 1mtr black length | thru Copper cable 16 sqmm and 1.25mtr red 1mtr black length
67 | Mains connection |  | 3 core copper cable size 0.75sqmm, 1 .5mtr length with TOP |  |  |  |  | Terminal 30A
68 | Output |  | 3pin socket 16A |  |  |  |  | Terminal 30A
69 | MCB in battery path |  | NA
70 | Fuse in battery path |  | External Fuse
71 | MCB in Solar path |  | NO
72 | Fuse in Solar Path |  | Yes
73 | Grid By pass Manually |  | Through switch
74 | Input Protection |  | Resettable Circuit breaker
75 | Front panel Switch Detail RESET* -Optional

## Table 3
1 | Charging Current Low High Setting
1A. On Pressing "SET" button once - Charging Current present Setting will be displayed.
1B. While "Charging Current" setting is displayed, pressing the "CHANGE" button will alternate between the available charging current options. Charging current will have two options "LO" and "HI" as displayed above.Default value "HI".
2 | Battery Selection
2A. On pressing "SET" button again, selected "BATTERY TYPE" will be displayed.
2B. The "BATTERY TYPE" selection will have four options - TUB (Tubular Battery), FLT (Flat Plate Battery), SF (SMF or VRLA Battery), GEL (Tubular Gel battery). While the selected battery type is displayed, on pressing "CHANGE" button will alternate between the four available options in the order listed above.Default value "TUB".
3 | Solar Mode Selection
3A. On Pressing "SET" button once - Solar Mode present Setting will be displayed.
3B. While "Solar Mode" setting is displayed, pressing the "CHANGE" button will alternate between the available solar mode options. Solar Mode will have Three options "HC" (Quick Charging Mode), "EC"(Ecomomic Charging Mode) and "SC" (Smart Charging Mode) as displayed above.Default value "HC".
4 | Grid Charging Mode Enable/Disable
4A. On Pressing "SET" button once - Grid Charging Enable/Disable present Setting will be displayed.
4B. While "Grid Charging Mode" setting is displayed, pressing the "CHANGE" button will alternate between the available charging mode options. Charging mode will have two options "GCE(Grid Charging Enable)" and "GCD(Grid Charging Disable)" as displayed above.Default value "GCE".
5 | Grid Reconnect Voltage mode in Solar Power Saving Mode (EC)
5A. On Pressing "SET" button once - Grid Reconnect voltage present Setting will be displayed.
5B. While "Grid Reconnect voltage Mode" setting is displayed, pressing the "CHANGE" button will alternate between the available Reconnect battery voltage options. Reconnect battery voltage will have two

## Table 4
options "11.8" and "11.2" as displayed per battery above.Default value "11.8".
6 | UPS / INVERTER Mode Selection
6A. On Pressing "SET" button once - UPS/Inverter present Setting will be displayed.
6B. While "UPS/INVERTER MODE" setting is displayed, pressing the "CHANGE" button will alternate between the available Setting options. UPS/Inverter will have two options "UPD" ( UPS Mode Disable) and "UPE" (UPS Mode Enable) as displayed per battery above.Default Selection is "UPD".
Note: RESET Switch - If Switch is press for 5Sec and release after beep sound then the all setting wil be resetted to default value