## Sheet1
SOLAR HYBRID INVERTER & PCU WITH MPPT TECHNICAL SPECIFICATION
S. No. | Parameter | Units
1 | Model Name |  | SunSine Max 1500 | SunSine 2500 | SunSine 3000 | SunSine 3500 | SunSine 5500
2 | Rating |  | 1100 | 2100 | 2500 | 3000 | 5000
3 | Operating Voltage | Volts | 12 | 24 | 24 | 48 | 48
SPV Parameters
4 | SPV Open Circuit Voltage Range (Min-Max) | Volts | 18-45 | 36-90 | 36-90 | 72-180 | 72-180
5 | Max Power SPV | KW | 1 | 2 | 2 | 3.5 | 5.5
6 | Compatible SPV Panels |  | 36 /60 / 72 Cell
MPPT Based Charge Controller
7 | Switching Element |  | IGBT Module
8 | Controller |  | DSP
9 | Efficiency |  | >95%
10 | Battery Charging Stages |  | 5 (Softstart, Boost, Absorbtion, Float, Equalise)
Battery
11 | Low Cut off | Volts | 10.5/Battery +/-2%
12 | Low Cut off Recovery | Volts | 11.5/Battery +/-2%
13 | Low Buzzer | Volts | 10.7/Battery +/-2%
14 | High Cut off | Volts | 15.5/Battery +/-2%
15 | High Cut off Recovery | Volts | 15.0/Battery +/-2%
16 | Boost Charging Volt by SPV (TUB) | Volts | 14.5/Battery +/-2%
17 | Boost Charging Volt by Grid (TUB) | Volts | 14.0/Battery +/-2%
18 | Charging Current by Grid | Amps | 18A +/- 2%
19 | No Load Battery Current | % | 0.02
Output
20 | Output @ No load | Volts | 230 +/- 2%
21 | Output Frequency | Hz | 50 +/- 2%
22 | Overload | Amps | 3.5 | 7 | 7 | 10.5 | 17.4
23 | Overload | Watts | 800 W | 1.6 KW | 1.6 KW | 2.4 KW | 4 KW
24 | Output Low Retry | - | 1 Time
25 | Output Short Circuit | - | 1 Time
Grid
26 | No of Phase | - | 1 Phase - 3 Wire P.N,E
27 | Voltage Range (Inverter Mode) | V | 100-280 +/-2%
28 | Voltage Range (UPS Mode) | V | 175-255 +/-2%
29 | Frequency Range | Hz | 45-55 +/-2%
Display
30 | Display |  | 16x2 LCD |  | 20x4 LCD
31 |  | Output (Inverter) | Voltage, Current, Power and Frequency
32 |  | Input (Grid) | Voltage and Frequency
33 |  | Solar | Voltage, Current, Power and Energy (Optional)
34 |  | Battery | Voltage, Current
35 |  | Status/Faults | Inv Status, Main Status, Charge status, Solar status, and Battery Status/charging stages
Inverter
36 | Switching Element | - | MOSFET
37 | Output Voltage | Volts | 220
38 | Phase | - | 1Phase-3Wire P,N,E
39 | Output Waveform | - | Digitally Filtered Pure Sine Wave
40 | Frequency | Hz | 50 +/-2%
41 | Changeover (Mains to Inverter) | ms | <10ms
42 | Output Power Factor | Pf | 0.8
43 | Overload Retry | - | 3 times / 5 times
44 | Switches | - | System ON/OFF, Mode Selection : Hybrid /PCU/Smart INV/ UPS Selection
45 | Indication (LED) | - | Inverter On, Mains in Range, Battery Low/High, Charger On, Overload, Faults
46 | Alarm (Audible) | - | Battery Low, Overload, Charger On, Inverter On, Solar Charger On
47 | Protection | - | Overload, Short Circuit Protection, Over Voltage, SPV Surge, and Transit Protection (MOV Varistors), Reverse Polarity of Battery , Over temperature protection, Under voltage, and over voltage protection
48 | Cooling | - | Forced Air Cooling (Temp Controlled)
49 | Communication
50 | Operating Temp | C | 0-50
51 | Operating Humidity | % | 95
52 | Protection class | - | IP20
53 | Dimension LXWXH | mm | 355x330x205 | 355x330x205 | 355x330x205 | 510x460x305 | 510x460x305
54 | Weight | Kg | 18 | 21 | 31.5 | 40 | 52